## Slide 1: Analysis of Power Resilience for Outdated Residential Power Distribution Systems in Realistic Operating Conditions
Chengwei Lei, Noah Pitts, Ruting Jia, and Weisong Tian

## Slide 2: Backgrounds
Thermal-magnetic circuit breakers (TMCB) are the most-commonly used type of circuit breakers in the user-end power distribution panels.
Power distribution panels are often spotted outdoors, especially in the old residential areas and deployable microgrids (e.g., refugee camps and military camps).

## Slide 3: Background: TMCB
TMCB has two protection functions: thermal tripping and magnetic tripping.
Thermal tripping allows overloads to exist for a relative longer period
Magnetic tripping cuts off the circuit immediately when fault happens
The time-current-curve (TCC) provided by the manufacturer is used in creating the thermal model for the TMCB

## Slide 4: Background: Probability-based TMCB modeling
Thermal tripping time is determined by a probability pattern [4]

## Slide 5: Challenges
The TCC from the manufacturers are often obtained in ideal indoor environment (commonly 25).
The surface temperature of the outdoor power distribution panels can get very hot (possibly 65 or higher [3]).
The thermal tripping heating process in real-life may vary from the TCC. They may be tripped at a lower overload current than the TCC indicates.
Circuit breakers are reusable. Used circuit breakers with loose/fatigue mechanical components that may lead to unexpected trips.
These unexpected trips are called as nuisance tripping.

## Slide 6: Objectives
In this work, we plan to construct simulation models for TMCBs with the following factors considered:
Ambient temperature
Used conditions
Substandard products
These factors will change the tripping characteristics for the TMCB. Our goal is to integrate these factors into our TMCB simulation model [4], so that the real-world operating characteristics can be shown.

## Slide 7: Tripping current change in high ambient temperature
Experiment data suggests that higher operating temperature will lead to lower tripping current [1].
According to the experiment data in [1], the tripping current decrease varies by model and capacity of the TMCB.
The greatest decrease that recorded in [1] was 0.671% per 1 above 25.
Our goal is to summarize the experimental data and implement it to the thermal-based TMCB simulation model.

## Slide 8: Modeling of tripping current in high operating temperature
The following equation is used to estimate the actual tripping current given the operating temperature and the rated current:
is the operating temperature in Celsius, is the rated current of the TMCB, and the four parameters are to be determined.
To get the best estimation of the parameter matrix, we minimize the total error by Root Mean Squared Error (RMSE), which is calculated as
Environmental vector
Physical model vector
Parameter matrix

## Slide 9: Example
We applied this method on the experimental data (Brand 3 in [1]), and we applied the exhaustive search method to determine the most optimal combination of the four unknown parameters, i.e., The change of these parameter with the RMSE is shown in the following diagrams.
Clearly, we can take the combination when the RMSE reaches its minimum value in these two diagrams, respectively.
The optimization results for this example are:

## Slide 10: Nuisance tripping in used conditions
Used TMCB may have loose or fatigue mechanisms inside, which may cause inaccurate tripping in application.
In the work [2], over 3,000 used TMCB that were installed between 1950s to 2014 were tested. Following the UL489 Standard, and assuming a 0.3% failure rate, the brand new TMCB’s tripping current should follow a normal distribution of the rated current.
However, the worn TMCB has shown a “flatter” and shifted normal distribution. By applying the exhaustive search method, the worn TMCB’s tripping current will follow of the rated current.
We can apply the following equation to the TMCB simulation model to show the used conditions ( and are the shift and flat ratio of the given worn TMCB):

## Slide 11: Substandard TMCB
Substandard, poor-quality TMCB are often spotted in the market, especially in the aged and under-maintained buildings.
  By analyzing the data collected in [2], the thermal tripping pattern of these substandard TMCB follows a similar trend as the worn TMCB,
  The proportion of “failed to trip” outliers may significantly increase.
    We have observed a 24.3% increase of such outliers,
  It may increase the chance of fire hazard.

## Slide 12: Simulation example
In this work, we simulate a power distribution system that has a 50-A TMCB installed outdoors, while three 15-A TMCB were installed indoors. Without considering the temperature factor, under full-rated load, the 50-A TMCB should not be tripped.
We assume the outdoor TMCB were very hot at 65 while the indoor TMCB were at 25We simulate for two hours which represents typical hot summer afternoons. We found that there are 6 nuisance trips among 100 trials because of the high operating temperature, and if the TMCB were used, this number increases to 8 according to our simulation experiments.

## Slide 13: Some of the references in this paper
[1] J. Aronstein, “Temperature sensitivity of residential molded case circuit breakers,” IEEE Access, vol. 7, pp. 38 714–38 720, 2019.
[2] J. Aronstein and D. W. Carrier, “Molded case circuit breakers-some holes in the electrical safety net,” IEEE Access, vol. 6, pp. 10 062–10 068, 2018.
[3] Y. Lv, A. Huang, J. Yang, J. Xu, and R. Yang, “Improving cabin thermal environment of parked vehicles under direct sunlight using a daytime radiative cooling cover,” Applied Thermal Engineering, vol. 190, p.116776, 2021.
[4] C. Lei and W. Tian, “Probability-based customizable modeling and simulation of protective devices in power distribution systems,” Energies, vol. 15, no. 1, p. 199, 2021.

## Slide 14: Thank you!
Questions?